| Inspection Date | 27-2-2023 | Report Walkthrough. | MACINS06 27/2/2023 |
| --- | --- | --- | --- |
| Site Name | Main Campus | Location | Building D |
| Inspected By | Navaz | Witnessed by |  |

| Inspection Type | General Housekeeping & Sanitation Fire Electrical Ladders Lab Food Structure Motor Vehicles Landscaping PPE Stores Emergency Evacuation |
| --- | --- |

| S/N | Description | Risk Evaluation |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Low | Med | High |
|  | Distribution box in electric room D05039 found not covered. |  |  |  |
|  | One of lights not working in IDF room D05040 |  |  |  |
|  | Cigarette butts found in fourth floor (attached photo) -4th floor |  |  |  |
|  | Exit light not working in the corridor -4th floor near male wash room |  |  |  |
|  | Protruding steel channels may cause injury to passer-by -4th floor |  |  |  |
|  | Housekeeping not done in one of the room. |  |  |  |
|  | Schuko socket /adapter not used in indoor basket ball court -4th floor D04101 |  |  |  |
|  | The mobile of contractor was found to be charging in Electric room D02044 |  |  |  |
|  | Fire extinguisher found hindered in shell & core are in 2nd floor |  |  |  |
|  | There is difficulty in opening fire extinguisher cabinet door near D01051A |  |  |  |
|  | Trolley found kept in GF D Bldg Electrical room. |  |  |  |

| Attachment | Photos Video Footage Other |
| --- | --- |

| S/N |
| --- |
|  | Action | By Whom |  | By When |
|  | Distribution box in electric room D05039 to be covered. | FM-Hard | 15-3-23 |  |
|  | One of lights that is not working in IDF room D05040 to be replaced. | FM-Hard | 15-3-23 |  |
|  | Cigarette butts found in fourth floor (attached photo) -4th floor to be removed | FM-soft | 15-3-23 |  |
|  | Exit light not working in the corridor -4th floor near male wash room to be rectified | FM-Hard | 15-3-23 |  |
|  | Protruding steel channels may cause injury to passer-by -4th floor to be removed | FM-Hard | 15-3-23 |  |
|  | Housekeeping to be done in one of the twin room. -4th floor ( see photo) | FM-soft | 15-3-23 |  |
|  | Schuko socket /adapter to be used in indoor basket ball court -4th floor D04101 | FM-Hard | 15-3-23 |  |
|  | Electric room D02044 to be secured | FM-Hard | 15-3-23 |  |
|  | Easy access to be provided for Fire extinguisher in shell & core area in 2nd floor | FM-soft | 15-3-23 |  |
|  | Easy opening of fire extinguisher cabinet door near D01051A to be ensured | FM-Hard | 15-3-23 |  |
|  | Trolley in the corridor of electric room to be removed. | FM-soft | 15-3-23 |  |

Attached Photos