## Findings
EHS Internal Audit Findings
No | Location | Department | Lab | Reference No | Clause | Observation | Finding
[7 empty] | Major | Minor | Area of improvement
1 | Main Campus | EHS | AFEHS | AFEHS-EHS/REP M01 -17/Oct/2022 | ISO45001:2018 6.1.1 | The latest protocol procedure of COVID from MOE found not included in the EHS legal register. | 0 | 1 | 0
3 | Main Campus | EHS | AFEHS | AFEHS-EHS/REP M02-17/Oct/2022 | ISO14001:2015 8.2.d | The mock drill plan for different scenarios ( such as Chemical spill ) for 2022 is not uniformly spread on the first half of the year 2022 | 0 | 1 | 0
5 | Main Campus | EHS | AFEHS | AFEHS-EHS/REP M03-17/Oct/2022 | ISO 50001:2018 7.2.d | The competency record of EHS team involved in EnMS not retained ( EnMS lead implementation Certificates) | 0 | 1 | 0
7 | Main Campus | EHS | AFEHS | AFEHS/REPM03A-17/Oct/2022 | ISO 45001 9.1.1 | The performance evaluation on third quarter of EHSMS not carried. | 0 | 0 | 1
8 | Main Campus | Civil Engineering | G02017 | AFEHS-EHS /REP M04-18/OCT/2022 | ISO 45001 8.1, OSHAD COP#36 3.1.1.b.x | Servicing / PPM / calibration record for Autoclave not available. | 0 | 1 | 0
9 | Main Campus | Civil Engineering | G02017 | AFEHS-EHS /REP M04-18/OCT/2022 | OSHAD COP#01 3.1.1.g | The chemical inventory list not found updated (last done on Sep 2021). | 0 | 1 | 0
10 | Main Campus | Mechanical Engineering | C00061 | AFEHS-EHS /REP M05-18/OCT/2022 | ISO 45001 7.2.b | Teaching assistants have not undertaken additional external First Aid Training. ( Minor Non Conformity) | 0 | 1 | 0
11 | Main Campus | Mechanical Engineering | C00062 | AFEHS-EHS /REP M05-18/OCT/2022 | ISO 45001 7.2.d | The training records of EHS online mandatory training courses not available in file ( Minor Non Conformity) | 0 | 1 | 0
12 | Main Campus | Mechanical Engineering | C00063 | AFEHS-EHS /REP M05-18/OCT/2022 | ISO 45001-6.1 | Task specific risk assessment prepared for equipment not reviewed by EHS dept. | 0 | 1 | 0
13 | Main Campus | Mechanical Engineering | C00064 | AFEHS-EHS /REP M05-18/OCT/2022 | OSHAD Cop #17 3.4.b | RACE Safety signage not found in the lab | 0 | 0 | 1
14 | Main Campus | Industrial Systems Engineering | Academic Laboratories | AFEHS-EHS /REP M06-18/OCT/2022 | ISO 45001 7.4.2.a | Departmental meeting, as part of internal communication, to have EHS issues /concerns discussed as an agenda. ( Opportunities for Improvement) | 0 | 0 | 1
15 | Main Campus | Industrial Systems Engineering | Academic Laboratories | AFEHS-EHS /REP M06-18/OCT/2022 | OSHAD Cop #15 3.4.b | Proper grounding to be provided such as Schuko adapters for equipment. | 0 | 1 | 0
16 | Main Campus | Industrial Systems Engineering | Academic Laboratories | AFEHS-EHS /REP M06-18/OCT/2022 | ISO 45001-6.1 | Task Specific Lab risk assessment in labs to be reviewed /approved. | 0 | 1 | 0
17 | Main Campus | Industrial Systems Engineering | Academic Laboratories | AFEHS-EHS /REP M06-18/OCT/2022 | OSHAD Cop #15 3.4.C | Earthing continuity test report from Imdaad to be obtained. The path to earth from circuits, equipment, and enclosures shall be permanent, continuous, and effective. | 0 | 1 | 0
18 | Main Campus | Electrical & Computer Engineering | C-02009 | AFEHS-EHS /REP M07-19/OCT/2022 | OSHAD Cop #17 3.4.b | Fire extinguisher & Power shut-off Safety signage not adequately pasted in the lab. The lab door signage not updated. | 0 | 0 | 1
19 | Main Campus | Electrical & Computer Engineering | C-02009 | AFEHS-EHS /REP M07-19/OCT/2022 | ISO 45001-8.2 | The awareness document of responding to different emergency- student fainting, Electrical shock, water leakage, fire in near-by labs-etc.,) scenarios by students not found. | 0 | 1 | 0
20 | Main Campus | Electrical & Computer Engineering | C-02009 | AFEHS-EHS /REP M07-19/OCT/2022 | OSHAD Cop #15 3.4.C | Earthing continuity test report for lab not available. | 0 | 1 | 0
21 | Main Campus | Biomedical Engineering | L01026 | AFEHS-EHS /REP M08-18/OCT/2022 | OSHAD COP#01 3.1.1.f | The list of carcinogen, mutagens & teratogens used in lab not identified ( Eg., Benzyl Chloride) & to be kept separately / used in lab as per SOP for carcinogens. | 0 | 1 | 0
22 | Main Campus | Biomedical Engineering | L01026 | AFEHS-EHS /REP M08-18/OCT/2022 | ISO 45001-6.1 | Specific lab risk assessment available, but not updated. | 0 | 1 | 0
23 | Main Campus | Biomedical Engineering | L01026 | AFEHS-EHS /REP M08-18/OCT/2022 | ISO 45001- 8.1 | List of authorized lab users not available during the audit. | 0 | 0 | 1
24 | Main Campus | Biology Lab | B01087 | AFEHS-EHS /REP M09-18/OCT/2022 | ISO 45001 8.2 | The Emergency shower was not founded inspected last month. Last inspection done in August-22. | 0 | 1 | 0
25 | Main Campus | Robotics | B04042 | AFEHS-EHS /REP M010-19/OCT/2022 | ISO 45001 6.1.2 | The lab door was found kept wedged open allowing unauthorized entry inside labs. | 0 | 0 | 1
26 | Main Campus | Robotics | B04042 | AFEHS-EHS /REP M010-19/OCT/2022 | UAE life safety code | The smoke detectors were found to be masked | 0 | 1 | 0
27 | Main Campus | Robotics | B04042 | AFEHS-EHS /REP M010-19/OCT/2022 | ISO 45001-8.2 | The exit route was found to be blocked with materials | 0 | 1 | 0
28 | Main Campus | Robotics | B04042 | AFEHS-EHS /REP M010-19/OCT/2022 | Lab Safety Manual 5.2 | Housekeeping was found to be poor in Control Room & Plant room | 0 | 0 | 1
29 | Main Campus | Robotics | B04042 | AFEHS-EHS /REP M010-19/OCT/2022 | Lab Safety Manual 5.9.4 | Unauthorized extension cords were found to be used in Control room. | 0 | 0 | 1
30 | Main Campus | Procurement-Management Store | Procurement & Contracts | AFEHS-EHS /REP M011-20/OCT/2022 | ISO 45001 7.2. | Technicians working in Management store not aware of lifting techniques, spillage response & first Aid. | 0 | 1 | 0
31 | Main Campus | Procurement-Management Store | Procurement & Contracts | AFEHS-EHS /REP M011-20/OCT/2022 | ISO 14001 7.4.3 | Communication regarding the safety guidelines for chemical ,Gas cylinder or equipment suppliers not available | 0 | 0 | 1
32 | Main Campus | Procurement-Management Store | Procurement & Contracts | AFEHS-EHS /REP M011-20/OCT/2022 | ISO 14001-8.2 | Distribution Gas Cylinder / tracking mechanism not available in the campus . | 0 | 0 | 1
33 | Main Campus | Imdaad | Contractor | AFEHS-EHS /REP M012-20/OCT/2022 | OSHAD COP#01 3.1.1.f | EHS Auditing Plan of Sub contractor not available. | 0 | 0 | 1
34 | Main Campus | Imdaad | Contractor | AFEHS-EHS /REP M013-20/OCT/2022 | ISO 45001 6.1.2.2 | List of critical activities under Imdaad that affect OH&SMS not available | 0 | 0 | 1
35 | Main Campus | Westcoast | AFEHS | AFEHS-EHS /REP M014-20/OCT/2022 | ISO 14001 9.2.1 | Subcontractor Audit plan not found | 0 | 0 | 1
36 | Main Campus | Westcoast | AFEHS | AFEHS-EHS /REP M014-20/OCT/2022 | ISO 14001 9.2.2 | Action item tracking Register not found. | 0 | 1 | 0
37 | Main Campus | FM Department | AFEHS | AFEHS-EHS /REP M015-20/OCT/2022 | ISO 50001 9.1.1.a.3 | Real Time Energy Performance Monitoring of Significant Energy Use Equipment ( Chillers, Cooling Tower & package units) not available | 0 | 1 | 0
38 | Main Campus | FM Department | AFEHS | AFEHS-EHS /REP M015-20/OCT/2022 | ISO 14001 8.1 | Action plan to phase out HCFC refrigerant not available in file | 0 | 0 | 1
39 | Main Campus | FM Department | AFEHS | AFEHS-EHS /REP M015-20/OCT/2022 | ISO 14001-9.1 | IAQ test done but recent report not available in file. | 0 | 0 | 1
40 | Main Campus | FM Department | AFEHS | AFEHS-EHS /REP M015-20/OCT/2022 | ISO 45001-7.2 | Specialized gas technician for replacement of cylinder in both campuses not available. | 0 | 1 | 0
41 | SAN Campus | Chemical Engineering | 3021 | AFEHS-EHS /REP S_01-17/OCT/2022 | ISO 45001 7.3 | First Aider list not available & refresher training if required for all lab representatives. | 0 | 1 | 0
42 | SAN Campus | Chemical Engineering | 3021 | AFEHS-EHS /REP S_02-17/OCT/2022 | ISO 45001 8.2.1 | Protective measures i.e. emergency push button found blocked/inaccessible. Fire extinguisher placed inappropriate area on floor. | 0 | 1 | 0
43 | SAN Campus | Chemical Engineering | 3021 | AFEHS-EHS /REP S_03-17/OCT/2022 | ISO 45001 8.2.1 | Safety Data Sheets not available for Gas cylinders. | 0 | 1 | 0
44 | SAN Campus | Chemical Engineering | 3021 | AFEHS-EHS /REP S_04-17/OCT/2022 | ISO 45001 7.3 | Lab user is not aware on KU Risk Management Procedure for categorizing the risk of lab activities. (Opportunity for improvement) | 0 | 1 | 0
45 | SAN Campus | Chemical Engineering | 3021 | AFEHS-EHS /REP S_05-17/OCT/2022 | OSHAD CoP #15 3.4.C | Earthing continuity test report for lab not available. | 0 | 1 | 0
46 | SAN Campus | Core Labs | 8017 | AFEHS-EHS /REP S_06-18/OCT/2022 | ISO 45001 7.3 OSHAD E 02 3.1 (a) | Lab staff is not aware on KU Risk Management Procedure for categorizing the risk of lab activities. | 0 | 1 | 0
47 | SAN Campus | Core Labs | 8017 | AFEHS-EHS /REP S_07-18/OCT/2022 | ISO 45001 7.3 OSHAD E 02 3.1 (a) | Lack of awareness regarding accessing EHS resources from KU portal. | 0 | 1 | 0
48 | SAN Campus | Core Labs | 8017 | AFEHS-EHS /REP S_08-18/OCT/2022 | ISO 45001 8.1.2 | Unsuitable adaptor used for equipment electrical connection. | 0 | 1 | 0
49 | SAN Campus | Core Labs | 8017 | AFEHS-EHS /REP S_09-18/OCT/2022 | OSHAD CoP #15 3.4.C | Earthing continuity test report for lab not available. | 0 | 1 | 0
50 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_10-18/OCT/2022 | ISO 45001 7.3 OSHAD E 02 3.1 (a) | Lab staff is not aware on KU Risk Management Procedure for categorizing the risk of lab activities. | 0 | 1 | 0
51 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_11-18/OCT/2022 | ISO 45001 6.1.2 | The lab door was found kept open allowing unauthorized entry inside labs. | 0 | 1 | 0
52 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_12-18/OCT/2022 | ISO 45001 7.3 | Lack of awareness regarding accessing EHS resources from KU portal. | 0 | 1 | 0
53 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_13-18/OCT/2022 | ISO 45001 8.2 | Emergency exit signage is not available. | 0 | 1 | 0
54 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_14-18/OCT/2022 | ISO 45001 8.1.2 | PPE is improperly placed. | 0 | 1 | 0
55 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_15-18/OCT/2022 | ISO 45001 7.3 | First Aider Training not received. | 0 | 1 | 0
56 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_16-18/OCT/2022 | ISO 45001 9.1 | Fume hood #3 alarm issue, inspection and maintenance to be ensured. | 0 | 1 | 0
57 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_17-18/OCT/2022 | ISO 45001 6.1.2.2 | Liquid chemicals stored in normal fume hood cabinet. | 0 | 1 | 0
58 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_18-18/OCT/2022 | ISO 45001 6.1.2.1 | Secondary containment not observed for liquid chemicals. | 0 | 1 | 0
59 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_19-18/OCT/2022 | ISO 45001 6.1.1 | Task Specific risk Assessment for some experiments not available. | 0 | 1 | 0
60 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_20-18/OCT/2022 | ISO 45001 9.1 | Exhaust Ventilation for chemical cabinets not provided. | 0 | 1 | 0
61 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_21-18/OCT/2022 | ISO 45001 8.1.2 | Display GHS Pictogram signage to create awareness among students. | 0 | 0 | 1
62 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_22-18/OCT/2022 | Lab Safety Manual 4.1 | “Undertaking from students” that they will comply with lab safety procedures not found. | 0 | 1 | 0
63 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_23-18/OCT/2022 | ISO 45001 8.2 | The awareness document of responding to different emergency- student fainting, Electrical shock, water leakage, fire in near-by labs-etc.,) scenarios by students not found. | 0 | 1 | 0
64 | SAN Campus | Chemistry | 8018 | AFEHS-EHS /REP S_24-18/OCT/2022 | OSHAD CoP #15 3.4.C | Earthing continuity test report for lab not available. | 0 | 1 | 0
65 | SAN Campus | Core Labs | 8025 | AFEHS-EHS /REP S_25-19/OCT/2022 | ISO 45001 7.3 | Lab staff is not aware on KU Risk Management Procedure for categorizing the risk of lab activities. | 0 | 1 | 0
66 | SAN Campus | Core Labs | 8025 | AFEHS-EHS /REP S_26-19/OCT/2022 | ISO 45001 7.5.3 | Updated soft copy of reviewed Risk Assessment available. Outdated RA hardcopy filed. | 0 | 1 | 0
67 | SAN Campus | Core Labs | 8025 | AFEHS-EHS /REP S_27-19/OCT/2022 | ISO 45001 6.1.2 | The lab door was found not locked and it will create unauthorized entry inside labs. | 0 | 1 | 0
68 | SAN Campus | Core Labs | 8025 | AFEHS-EHS /REP S_28-19/OCT/2022 | ISO 45001 8.2 | Fire alarm hooter is not available inside the lab. Lab team has concern on hearing the fire alarm from corridor during the operation of lab equipment. Lab team has notified the concern to the FM. | 0 | 0 | 1
69 | SAN Campus | Chemical Engineering/ CMAT | 8130 | AFEHS-EHS /REP S_29-19/OCT/2022 | ISO 45001 7.3 | Lab staff is not aware on KU Risk Management Procedure for categorizing the risk of lab activities. | 0 | 1 | 0
70 | SAN Campus | Chemical Engineering/ CMAT | 8130 | AFEHS-EHS /REP S_30-19/OCT/2022 | ISO 45001 8.1.2 | Solid chemicals segregation is poor. | 0 | 1 | 0
71 | SAN Campus | Chemical Engineering/ CMAT | 8130 | AFEHS-EHS /REP S_31-19/OCT/2022 | Lab Safety Manual 5.9.4 | Unauthorized extension cords were found to be used in Control room. | 0 | 1 | 0
72 | SAN Campus | Chemical Engineering/ CMAT | 8130 | AFEHS-EHS /REP S_32-19/OCT/2022 | ISO 45001 7.3 | First Aider Training not received. | 0 | 1 | 0
73 | SAN Campus | Chemical Engineering/ CMAT | 8130 | AFEHS-EHS /REP S_33-19/OCT/2022 | ISO 45001 6.1.2.1 | Secondary containment not observed for liquid chemicals storage. | 0 | 1 | 0
74 | SAN Campus | Chemical Engineering/ CMAT | 8130 | AFEHS-EHS /REP S_34-19/OCT/2022 | OSHAD CoP #15 3.4.C | Earthing continuity test report for lab not available. | 0 | 1 | 0
75 | SAN Campus | Petroleum Engineering | 3137 | AFEHS-EHS /REP S_35-19/OCT/2022 | ISO 45001 7.3 | First Aider certificate is expired. Refresher training required. | 0 | 1 | 0
76 | SAN Campus | Petroleum Engineering | 3137 | AFEHS-EHS /REP S_36-19/OCT/2022 | ISO 45001 7.3 | Emergency evacuation map is not displayed | 0 | 0 | 1
77 | SAN Campus | Petroleum Engineering | 3137 | AFEHS-EHS /REP S_37-19/OCT/2022 | ISO 45001 7.4.1 | Auditees are not sure about documentation on departmental activities. | 0 | 0 | 1
78 | SAN Campus | Petroleum Engineering | 3137 | AFEHS-EHS /REP S_38-19/OCT/2022 | ISO 45001 7.1 | Fire extinguisher hose nozzle damaged. | 0 | 1 | 0
79 | SAN Campus | Student Service Accommodation | Residence life office | AFEHS-EHS /REP S_39-19/OCT/2022 | ISO 45001 8.1.2 | There is no evidence of closing the EHS Inspection findings in regards to the accommodation. | 0 | 1 | 0
80 | SAN Campus | Student Service Accommodation | Residence life office | AFEHS-EHS /REP S_40-19/OCT/2022 | ISO 45001 7.3 | Employees are not aware of the incident reporting system in KU. | 0 | 0 | 1
81 | SAN Campus | Student Service Accommodation | Residence life office | AFEHS-EHS /REP S_41-19/OCT/2022 | ISO 45001 7.5.2 | Student Code of Conduct is not updated. | 0 | 1 | 0
82 | SAN Campus | Student Service Accommodation | Residence life office | AFEHS-EHS /REP S_42-19/OCT/2022 | ISO 45001 7.5.1 | Evidence of violation record is not provided. | 0 | 0 | 1
83 | SAN Campus | Administration | Administration | AFEHS-EHS /REP S_43-20/OCT/2022 | OSHAD Element 3 – 3.1.1 (f) | Inspection records for transportation, food retailers and catering are not available | 0 | 0 | 1
84 | SAN Campus | Administration | Administration | AFEHS-EHS /REP S_44-20/OCT/2022 | OSHAD Element 3 – 3.1.1 (f) | Training records for drivers , food handlers are not available | 0 | 0 | 1
85 | SAN Campus | Administration | Administration | AFEHS-EHS /REP S_45-20/OCT/2022 | OSHAD CoP 19- 3.1.1 (c) | Medical surveillance records for food handlers and drivers are not available | 0 | 0 | 1
86 | SAN Campus | HR | Training Department | AFEHS-EHS /REP S_46-20/OCT/2022 | OSHAD 3.1 Element 1 – Clause 3.1 | Measure employee conformance against EHS roles and responsibilities is missing | 0 | 1 | 0
87 | SAN Campus | HR | Training Department | AFEHS-EHS /REP S_47-20/OCT/2022 | OSHAD 3.1 Element 5- 3.2 (a) | Measurement of EHS general and specific competencies is missing | 0 | 1 | 0
88 | SAN Campus | Petroleum Geoscience | 3220 | AFEHS-EHS /REP S_48-18/OCT/2022 | ISO 45001-8.2 | Inability to illustrate EHS roles and responsibilities of lab engineers/lab custodian | 0 | 0 | 1
89 | SAN Campus | Petroleum Geoscience | 3220 | AFEHS-EHS /REP S_49-18/OCT/2022 | OSHAD Cop #17 3.4.b | Lab safety sign is outdated. | 0 | 1 | 0
90 | SAN Campus | Petroleum Geoscience | 3220 | AFEHS-EHS /REP S_50-18/OCT/2022 | ISO 45001-6.1 | General risk assessment is missing and task specific risk assessment is outdated | 0 | 1 | 0
91 | SAN Campus | Petroleum Geoscience | 3220 | AFEHS-EHS /REP S_51-18/OCT/2022 | ISO 45001 7.2.d | Unavailability of first aid training for lab engineers | 0 | 0 | 1
92 | SAN Campus | Physics Lab | 2141 | AFEHS-EHS /REP S_52-18/OCT/2022 | ISO 45001 6.1 | Unavailability of Lab General Risk Assessment | 0 | 1 | 0
93 | SAN Campus | Physics Lab | 2141 | AFEHS-EHS /REP S_53-18/OCT/2022 | ISO 45001 7.3 | Lack of awareness for Emergency call number (3999) | 0 | 0 | 1
94 | SAN Campus | Student Service Accommodation | Residence life office | AFEHS-EHS /REP S_54-20/OCT/2022 | ISO 45001 8.1.2 | There is no evidence of closing the EHS Inspection findings in regards to the Accommodation. | 0 | 1 | 0
95 | SAN Campus | Student Service Accommodation | Residence life office | AFEHS-EHS /REP S_55-20/OCT/2022 | ISO 45001 7.3 | Employees are not aware of the incident reporting system in KU. (Observation) | 0 | 0 | 1
96 | SAN Campus | Student Service Accommodation | Residence life office | AFEHS-EHS /REP S_56-20/OCT/2022 | ISO 45001 7.5.1 | Evidence of violation record is not provided. (observation) | 0 | 0 | 1
Total | [6 empty] | 0 | 64 | 29

## Positive points
Positive points
Lab Safety | New lab is being set up in compliance to EHS standards. | 1
| Lab door signage updated with lab engineer details. | 1
| The fume hoods and Biological safety cabinets were calibrated. | 1
| PPE’s required for lab activities are available | 1
Emergency Management | Emergency contact number posted on the lab. | 1
| Site Specific business continuity was evident during the audit | 1
| Site specific ERP was available during the Audit | 1
| The different emergency scenarios along with response procedure explained to all students on the first class of the lab. | 1
| Spill kit & First aid box available | 1
| Energy efficient lab equipment / accessories procured for labs. | 1
Training, Awareness and Competency | Student participant acknowledgement form signed and documented. | 1
| Training records of all lab users are available | 1
| Competent Fire warden and First aider were evident during the audit | 1
Operational planning and control General | Plumbers’ Hepatitis-B Vaccination details are available with the site team during the audit | 1
| Portable Appliance Test (PAT) for office equipment’s was found out during the audit. | 1
Inspection | Self-Inspection are conducted by lab engineer regularly | 1
| Half-yearly self-inspection by lab engineers carried out | 1
Risk Management | Risk assessment – General, specific & task specific risk assessment were all filed in a folder | 1
Measurement control | The PPM/Validation/servicing records of all lab equipment carried out as per manufacturers guidelines. | 1
| Monitoring & Measurement equipment’s calibration data are available. | 1
| PTW system is maintained and supporting documents was available during the audit. | 1
| Subcontractors MSRA was available during the audit | 1
Internal audit | Internal audit report and closed out was available during the audit. | 1
Document control | EHS documents all filed up with dividers and easily retrievable. | 1
Waste Management | Waste disposed as per KU waste disposal procedure. | 1
Communication | Monthly meeting organized with contractors to monitor EHS issues | 1
| Internal communication about OH&S is well organized and documented. | 1
Contractor Management | Subcontractor audit carried out for major contractors | 1
Roles and Responsibilities | All lab engineers were available during the internal audit showing their commitment. | 1
| Full cooperation from Lab Custodian Dr. Banu; Lab Engineer & researchers working in the lab. | 1
30

## Graphs
Non-confrmity
Major | 0
Minor | 64
Area of improvement | 29
Postive points | 30