## Sheet1
CHECK SHEET
INSTALLATION OF FIRE PUMP
Project: |  |  |  | Client :
Service Provider : |  |  |  | Building No.:
|  |  |  | Date.: |  | IR No.:
NO. | DESCRIPTION |  | CHECKED BY
|  |  | CONTRACTOR | SERVICE PROVIDER | CLIENT | REMARKS
1 | Diesel Fire Pump Capacity as per Approved MIR
2 | Fire pump which is same as per the approved submittal.
3 | Orientation of Diesel Pump is Correct (Suction & Discharge Line Correctly Piped)
4 | Check all the pipe works are all supported properly.
5 | Check the installation work as per the approved MS.
6 | Diesel Pump Control Panel Installed, Tested and on NORMAL Operation
7 | Check the clearance for access to the valves are provided.
8 | Complete required accessories to the line have been installed and provided.
9 | Check all the fasteners related to fire pump are tightened.
10 | Diesel Pump Tested and Properly Functioning
11 | Pressure Switch Adjusted and Tested to Required Pressure
12 | Diesel Pump Batteries Available and Fully Charged
13 | Diesel Tank is Installed and connected
14 | Diesel Tank Capacity is correct as per approved MIR
15 | Diesel Fuel Available
16 | Water Supply is Available
Remarks/Comments (if any):
Recommend to fix the Fire pump in closed air conditioned room
COMPANY |  | CONTRACTOR |  | Service Provider |  | CLIENT
Name
Designation
Signature
Date