2023

Internal Audit Department

Khalifa University of Science and Technology

June - 2023

Internal Audit Report

Review of Environment, Health and

Safety (EHS)

Ref: KU/2023/IAD-141

June 2023

Dr. Ebrahim Al Hajri

SVP Support Services

Khalifa University of Science and Technology

We have completed our review of the EHS Activity. The review was conducted during May – June 2023 covering the period from January 2022 to June 2023.

The objective of our audit was to review the adequacy and effectiveness of internal controls system and procedures; and to ensure compliance with operating policies and procedures, laws, regulations, and standards.

We have discussed the contents of our report, including our recommendations, with the respective processes’ owners and where relevant we have incorporated their comments and action plans to remediate our findings.

I would like to draw your attention to the issues highlighted in the executive summary, where opportunities for improvement were highlighted.

Yours Sincerely,

Abdulaziz Alkhoori

VP, Audit

Table of Contents

1.	Executive Summary	4

1.1 Introduction	4

1.2 Scope of Work	4

1.3 Audit Objectives	5

1.4 Audit Process	5

1.5  Summary of Audit Findings	5

2.	Background	7

3.	Detailed Audit Findings	8

4.	Appendix	18

- Executive Summary

  - Introduction

We have completed the Review of EHS, in line with the Approved Internal Audit Plan and Audit Engagement Memorandum Dated May 2023. The Internal Audit Findings / Improvement Opportunities to address associated risks / control gaps were identified and reported as part of this report.

  - Scope of Work

The Scope of Work comprised of the following areas:

Governance and Compliance

- Review existence of formally approved goals and objectives for the function.

- Verify existence / adequacy of governance structure including organizational structure, policies and procedures, delegation of authority matrix, Job descriptions, KPIs, etc.

- Review adherence to relevant policies and procedures.

- Review existence of Committee (s), charters and bylaws (If any).

- Review process of HSE accreditation and changes thereof.

- Review the management of records filing, storage, protection, access and retention.

- Review the compliance with UAE health and safety regulations and liaison with other Government entities for the administration of the EHSMS.

EHS Operations

- Review sufficiency of manpower in place to run the day-to-day activities undertaken by the Function.

- Verify existence/ adequacy of emergency response plan and assessing preparedness of the University Staff to react in emergency cases.

- Review the process of testing & reviewing emergency response procedures and maintaining emergency response equipment (including fire drills and firefighting equipment).

- Evaluate the management of HSE function at all campuses and coordination thereof.

- Check the existence of sufficient number of nurses with medical expertise to treat minor injuries or accidents.

- Verify the process of hazard identification and risk assessment.

- Review process in place for contractor's health and safety plans and activities (inspections and checks).

- Review the adequacy of communicating hazardous conditions to university community members including students, employees, and workers.

- Review controls over identification, storage, and disposal of hazardous waste.

- Check the adequacy of reporting, recording, investigating & analyzing incidents & injuries.

- Evaluate existence and adequacy of fire suppression system.

- Check the involvement of HSE personnel in the University events and assessing roles & responsibilities.

- Review the existence/ adequacy of training process to ensure employee, students, contractors and visitors’ awareness and skills necessary to fulfill their HSE obligations.

- Evaluate the ‘needs analyses, the process of identifying and evaluating needs in a community, Training Needs Analysis (TNA).

- Evaluate the process of HSE audits (Internal and External) to verify the conformance & the effectiveness of the HSE Management System.

- Review the field and research trips safety procedures in place.

- Assess the mechanism / reporting protocols in place for management reporting.

- Adequacy of general risk management and controls.

- Review of air monitoring processes as part of the air quality management system.

- Existence of process in place for monitoring noise in classrooms, laboratories, and workshops.

Others

- Review existence and relevance of departmental KPIs.

- Review the process to conduct Root cause analysis and develop action plans for KPIs not meeting targets.

- Verify departmental budget and reasons for over / under spend (if any).

  - Audit Objectives

The Objectives of the review are to independently review the system of internal controls, level of compliance with policies and procedures, and the achievement of the desired objectives.

  - Audit Process

The following are the key Audit Steps undertaken by the IA Department:

Planning

- Overview of the processes being reviewed.

- Key concerns in the activity to be reviewed.

- Key contact points for the review.

- Development of the Audit Program.

Execution

- Review and evaluate the soundness, adequacy, effectiveness and application of the operational, financial and administrative policies, systems and procedures.

- Review and evaluate the integrity, reliability and adequacy of planning and executing the operations.

- Identify gaps in control design and operating effectiveness as well as compliance with established policies, plans, procedures, laws, and regulations.

Reporting

- Prepare draft audit report on the adequacy and effectiveness of the control system and the efficiency with which processes are carried out.

- Submit draft audit report to the process owner recommending corrective actions to improve controls and operations.

- Conduct closing meeting to discuss and validate observations with process owner and help in developing action plans to mitigate risks.

  - Summary of Audit Findings

Controls need to be enhanced for 22% of the observations. A balance of 67% is within the moderate range and 11% is within the low range and needs to be monitored and prevented from entering the high-risk category and moderate range as applicable.

Please refer to Appendix 1 for detailed Ratings

The audit findings found during the review are summarized below. It should be noted that we have reported only on the exceptions detected during our review.

- Incident Management

The number of Incidents and Near Misses are inconsistent in the 3 lists maintained by EHS Function – List of incidents, EHS contractors’ statistics, and the OSHAD reports.

- EHS Site Visit

There were unsafe acts and unsafe conditions observed at site during the audit review. The following are summarized EHS site visit findings:

- Main Campus Findings

- Electrical room in E building was open and not locked to prevent unauthorized access.

- There was ongoing ‘working at height’ activity without a valid and approved PTW, and PPE which is a  non-compliance to the Personal Protective Equipment procedure and Permit to Work procedure

- Firefighting system diesel pump coolant level was “low”.  The coolant level should be at “High” level in the coolant tank scale.

- KU Vivarium project- PPE (Gloves, Helmet, safety belt, etc.) were not available during hammering nails activity, drilling activity, and working at height activity which is a non-compliance to the Personal Protective Equipment procedure

- SAN Campus Findings

- Firefighting system diesel pump coolant level was “low”.  The coolant level should be at “High” level in the coolant tank scale.

- In the campus clinic, Medicine "Diclogesic" was found expired in April 2023.

- The First Aider displayed in the chemical lab, was on leave and there is no alternate first aider number displayed which is a  non-compliance to Emergency Management Contingency Plan

- Unlabeled chemical containers are in the Chemical lab (3021)

- Arzanah building, the electrical room was open and not locked for unauthorized personnel.

- Background

The EHS Function is currently managed by the EHS Manager, who reports to the VP Administration, Facilities and EHS.  EHS is responsible for the wellbeing of students, faculty, staff, contractors, and visitors on the campuses, and for the campus environment. KU’s EHS Management System (EHS-MS) has been developed to meet the requirements of Abu Dhabi Emirate and relevant international standards (ISO). The EHS-MS aims to:

- Secure the health, safety, and welfare of KU community

- Protect the public from the health and safety risks from KU activities

- Eliminate workplace risks at the source

- Implement health, safety, security, and welfare standards

- Improve natural resource conservation and management

- EHS Function Structure

The organization structure for the EHS Function at KU has 10 staff members handling 5 roles as per the approved organization chart:

- Manager, Environment Health, and Safety

- EHS Compliance Senior Specialist

- Buildings Safety Specialist

- Labs Safety Specialist

- Labs Safety Senior Specialist

- EHS Main responsibilities

The main responsibilities of the EHS Function are as follows:

- Incidents Management & Reporting

- Evacuation and Emergency Drills

- Occupational Healthcare Monitoring

- Waste Management

- Hazard Identification and Risk Management

- EHS Trainings and Awareness

- Accreditations Compliance and Certifications

- EHS Audits and Inspections

- Fire Detection and Prevention

- Setting and Monitoring EHS Objectives

- Approval of Permit to Work

- EHS Positive Findings/Achievements

- Khalifa University won British Safety Council’s International Safety Awards 2022 with ‘Distinction’ for Health and Safety Measures

- The EHS team does not have major non-conformances in compliance with OSHAD and ISO requirements.

- Unsafe Practices observed by the EHS team were displayed and communicated as lessons learned.

- EHS Safety Code of Conduct and emergency instructions, were displayed in laboratories, kitchens, offices, etc. as an awareness communication.

- Emergency evacuation plans were displayed in each floor of each building to educate everyone about the emergency evacuation exits in case of any emergency.

- All firefighting and safety shower/wash equipment were inspected and tagged.

- Emergency drills were conducted as planned to cover all applicable emergency scenarios.

- Material Safety Data Sheets (MSDS) were available for all materials in labs.

| - Detailed Audit Findings |  |
| --- | --- |
|  Medium | - Policies & Procedures, Organizational Structure and Committees |
| Risk Ref : KU-EHS-01 & KU-EHS-02 |  |
| Observation/Process Enhancement Periodic Review / Update of EHS Policies and Procedures: As per the Document Control Procedure "KU–FD–EHS–MSM–08", Section 5.8.2, revision of the EHS Manual, Management System Manual (MSM) / Management Procedures Manual (MPM) / Division Procedures or Procedure Manual (DPM) should be: - At least once in four years or as and when found essential to ensure the effectiveness and continual improvement of the implemented Management System. - When there is a Significant Organizational Changes. It is pertinent to note that such updates in the EHS Manual ensure that the practices followed by all the staff and contractors are aligned with the latest EHS procedures and regulatory requirements. EHS team established EHS policies and procedures for the control of activities and EHS processes. However, during our review, we noted the following: - 4 policies and 33 out of 34 procedures (last review conducted in 2018) were not reviewed as per the frequency defined in Documents control Procedure. - Absence of Work at Height defined procedure. - First Aid Procedure does not cover expiry check of medical items due to which there was a non-compliance at site. - Electrical Safety procedure does not specify access controls of electrical rooms by only authorized personnel. Refer to Appendix 2 for further details. EHS Organization Structure Change: - EHS organization structure was updated in 2022 with a change in the EHS Manager and introduction of new roles (number of positions increased) such as one “Building Safety Coordinator” and one “EHS Specialist”. However, it was noted that the roles and responsibilities of EHS Building Safety Coordinator and EHS Specialists were not reflected in the policies and procedures, which may lead to ineffective implementation of EHS processes. - Review of MOC register - KU–FD–EHS–FOR–54 showed that the new EHS roles (Building Safety Coordinator and EHS Specialist) were not updated in the Management of Change (MOC) register which may expose KU to being non-compliant with ISO requirements. EHS Committee: As per OSHAD, Management System Elements V3.1, Section 3.2, the entity with greater than 50 employees shall establish Occupational Safety Health (OSH) Committee. OSH Committee meetings shall be recorded and conducted at a minimum of 4 times a year. The OSH Committee brings together management and employees/contractors to help create and maintain a safe workplace. It allows participation in development, implementation, and monitoring of the organization EHS policies and procedures. Further, this Committee enhances the investigation of EHS concerns and EHS reporting culture. However, we noted that the OSH Committee is not established leading to potential ineffective monitoring of EHS operations and thereby, ineffective implementation of EHS Management System and non-compliance with OSHAD. Recommendation - Ensure periodic review / update of EHS policies and procedures in line with Document Control Procedure i.e., post any organization changes and / or every four years (as a minimum). - Establish Work at Height Procedure, enhance the procedures for electrical safety to include access controls and update the first aid procedure to include checking of expiry date of medical items. - Maintain and update the MOC register with any changes in the organization structure, process, etc. - Establish the EHS Committee and conduct EHS committee meetings as per the frequency defined in OSHAD (4 times as a minimum). Management Action Plan Management Action Plan: Responsibility: Timelines: |  |
|  Medium | - EHS Objectives and Monitoring - ISO Requirements |
| Risk Ref : KU-EHS-04 |  |
| Observation/Process Enhancement EHS Objectives as per ISO 45001 Requirements: The EHS Objectives are set to ensure compatibility of EHS Function with the strategic direction of KU and in order to maintain and continually improve the EHS management system and performance. As per ISO 45001:2018, EHS objectives should take the following into account: - Results of the assessment of risks and opportunities. - Results of consultation with workers and workers representatives. It was noted that the EHS objectives of 2022 do not cover the above ISO 45001:2018 requirements, due to which the risks and opportunities may not be assessed leading to execution of unsafe activities without considering the hazards. Achievement of EHS Objectives: As per ISO 45001:2015, Section 6.2.2, when planning how to achieve its Occupational Safety and Health (OSH) objectives, the organization shall determine how the results will be evaluated, including the indicators for monitoring. During our review of 2022 EHS objectives - presented to KU management on 20th Dec 2022, it was noted that below 5 out of 13 EHS objectives were not achieved in 2022 in absence of any future corrective action plans and justifications: S/N; Objectives Details; Evidence Documents; Measuring Method; Target; Findings. 1; Achieve 100% compatibility with national standards; OSHAD certification and other EHS Standards.; 100% Compatibility; Dec 2022; Target Achieved for Main Campus. However, Target Not Achieved for SAN campus.. 2; Increase the recycle of general waste to 30%; General Waste Records on Monthly basis; Recycle 30 %; Dec-22; 26% achievement. No justification. 3; Target 3% reduction of Energy consumption from the previous year; 3% reduction target energy consumption/Monthly Report; 3% Energy Saving; Dec-22; Average Reduction in MAIN and SAN Campus is 2.5 %. No justification. 4; Complete full Integrated of Facilities Management CAFM Solution; Activation of EHS modules in CAFM system; 100% Completion; Jul-22; Target Not Achieved. 5; Develop Integrated Quality Management System and achieve ISO 9001 or more (ISO standard, APPA and RICS).; ISO Certification; 100% Completion; Dec-22; Target Not Achieved. Management Reviews of EHS activities: Management Review Meetings establishes the involvement and commitment of top management in the EHS activities. Management review meetings enables top management to assess EHS input/agenda to ensure safety of staff and identify any areas for improvements. As per ISO 45001:2018, the management review shall include the following: - The extent to which environmental objectives have been achieved - Information on the organization’s environmental performance, including trends - Monitoring and measurement results - Fulfilment of its compliance obligations - Audit results Our review of the Management Review Meeting conducted in Dec 2022 (once a year) showed that the ISO 45001:2018 coverage of the management review on areas such as achievement of environment objectives (e.g. Reduction of paper consumption, etc.), organization’s environmental performance, measurement results, compliance obligations and audits results (as shown above) were not met. This may lead to management not being aware of the current EHS performance, issues and compliance obligations. Refer to Appendix 3 for further details. Reporting of EHS Performance: EHS team generates an Annual Report showing the EHS performance, contractor performance, EHS statistics, and the KPI results. The annual EHS report establishes analysis of the overall EHS performance and EHS objectives and is required to be set to the management (VP Facilities and EHS) Our review showed that the 2022 Annual Report was not generated and recorded which may result in inadequate monitoring of EHS activities. Occupational Health and Safety Needs & expectations - Interested Party Register: As per ISO 45001:2018, Clause 4.2, Understanding the needs and expectations of workers and other interested parties, the organization shall determine: - Other interested parties, in addition to workers, that are relevant to the OSH management system. - Relevant needs and expectations (i.e., requirements) of workers and other interested parties. Our review of Interested Party Register showed that the Occupational Health and Safety related needs and expectations (e.g. Reporting of EHS statistics including incidents/near misses, contractors’ consultation and participation, etc.) were not adequately captured in the interested party registers. Further, visitor’s needs and expectations (e.g. EHS induction awareness, etc.) were not also captured in the interested party register. Such needs and expectations shall be defined to ensure clear identification and communication of requirements that visitors/other parties need to fulfil to comply with KU’s EHS management system. Internal and External Issues - Risk and Opportunities Register: As per ISO 45001:2018, Clause 6.1.1, actions to address risks and opportunities when planning for the OH&S management system, the organization shall consider the issues referred to interested parties and determine the risks and opportunities that need to be addressed. However, we noted that the organizational risks derived from Internal and External issues of Interested Parties were not captured as part of the risk and opportunities register (ROAR), which may lead to inadequate identification of EHS opportunities for improvements and business risks. Establish EHS Complaint Monitoring Mechanism As per the leading practice, EHS monitors and analyzes the occupational health related complaints and evaluate the repetitive events to minimize the risks and impacts. Currently, the complaints list is being monitored by the FM Department, which sends the complaints/work orders to EHS for closure. However, we noted inadequate mechanism adopted by EHS for tracking complaints and corresponding action plans in absence of adequate coordination with FM to provide reports / status on periodic basis. - Occupational Noise Requirements During our site visit to Arzanah Building - SAN Campus, we noted high compressor noise in the Analytical Chemistry and Biochemistry Core (ACBC) CORE lab. The Lab Specialist has complained about the high continuous noise during this audit. The EHS team are using a calibrated portable noise monitoring device. Latest Noise monitoring program was conducted in December 2021. As per OSHAD, Occupational Noise, the exposure monitoring shall be conducted by a competent, certified person to develop and implement a noise monitoring program and sampling strategy to assess the employees’ exposure to noise. The risk assessment shall be reviewed on a regular basis, at least annually and following any significant changes within the workplace likely to affect the noise levels employees are exposed to. However, there was no evidence of third-party noise monitoring certificate for the year of 2022 to showcase that the noise levels were checked and found to be within the safe limits which may in hearing loss hazards due to causes attributed to workplace and impacting wellbeing of employees and the contractors. Recommendation - Ensure the coverage of objectives such as assessment of risks & opportunities, worker consultation results, etc. while developing KU’s EHS Objectives. - Ensure achievement of EHS objectives and record justifications in case of non-achieved objectives. - Update the EHS Management Review Agenda to ensure coverage of requirements of ISO 45001:2018. - Ensure that the EHS Annual Report is generated on timely basis covering the key statistics around man-hours worked, number of workforce, Lost Time Injuries (LTIs), near-misses, property incidents, etc. Also, reports should be submitted to the management for monitoring of EHS activities. - Ensure that OSH related needs & expectations (such as Reporting of EHS statistics including incidents/near misses, contractors’ consultation, and participation, etc.) are defined in the interested parties register. - Ensure coverage of visitors needs and expectations (such as EHS induction awareness, etc.) in the interested parties register. - Ensure coverage of organizational risks derived from Internal and External issues in the risk & opportunities register. - Establish EHS complaints monitoring and analysis process investigate/analyze complaints and prevent re-occurrence. - Ensure EHS team gets access from IT for the monitoring the list of EHS work-orders and complaints. - Ensure noise monitoring process is effectively implemented and measured by a third party. Management Action Plan Management Action Plan: Responsibility: Timelines: |
|  Medium | - Hazard Identification and Risk Assessment |
| Risk Ref : KU-EHS-15 |  |
| Observation/Process Enhancement One of the "root causes" of workplace injuries, illnesses, and incidents is the failure to identify or recognize hazards that are present, or that could have been anticipated. A critical element of any effective EHS program is a proactive, ongoing process to identify and assess such hazards. As per OSHAD-SF- Technical Guideline - Process of Risk Management- V3.0, section 5.2, the organization shall identify who/what can be harmed or damaged and how, considering persons who may have additional difficulties such as new or expected mothers, people with special needs, young, or inexperienced workers. Our review of the Generic Risk Register showed the absence of hazard risk assessment considering the below requirements as per OSHAD: - Nurses’ availability/sufficiency. - New/expectant mothers. - Young workers including contractors. - Inexperienced workers including contractors. Recommendation Ensure adequate coverage of nurse’s availability, pregnant women, young and inexperienced workers while conducing hazard risk assessment to identify the risks associated with such hazards and to plan the applicable operational controls. Management Action Plan Management Action Plan: Responsibility: Timelines: |  |
|  High | - Incident Management |
| Risk Ref : KU-EHS-10 |  |
| Observation/Process Enhancement - Reporting of near-misses and Incidents on OSHAD’s Aladaa Portal: EHS Function reports the EHS performance statistics to OSHAD through al Aladaa portal on quarterly basis. During our review of OSHAD 2022 reports through Aladaa portal, it was noted that there were 7 near misses and 1 property damage reported to OSHAD, which are inconsistent with the number of near misses and incidents recorded as per the Contractor EHS Statistics (4 samples – 38 Near misses and 6 Incidents) and by the EHS team (4 Near misses and 1 Incident). Further, Property damage incident report issued on 6.9.2022, is not signed by the EHS manager/representative. Refer to Appendix 4 for further details. Recommendation - Ensure adequate and consistent recording and reporting of the incidents and near misses in the incident tracker, contractor EHS statistics reports and the OSHAD reports. - Establish process for EHS near miss reporting culture within the organization to encourage the students, employees, and contractors to report near misses and participate in investigating and applying action controls. - Ensure that EHS manager/representative signs and approves the incident investigation report to establish management commitment. Management Action Plan Management Action Plan: Responsibility: Timelines: |  |
|  Medium | - Training and Awareness |
| Risk Ref : KU-EHS-17 |  |
| Observation/Process Enhancement EHS Training Plan: Following the completion of the Training Need Analysis (TNA), the entity should summarize the needs in a training plan. The training plan should be designed to assist the entity in the management of the training and help to track progress of what has been completed. As per OSHAD-SF- Technical Guideline - Training, Awareness and Competency - V3.0, section 8, the Training Plan should contain the following: - Training courses required. - Frequency of training. - Planned dates. - Internal/external trainings. - Training completion date. Our review of the EHS records, documentation and process understanding meetings showed the absence of Training Plan in place to address the training aspects highlighted above. Incident / Near Miss Reporting Culture As per OSHAD-SF- Technical Guideline - Training, Awareness and Competency - V3.0, section 4, it is important that the Training Need Analysis (TNA) identifies any general training or awareness that all employees require such as incident reporting. And, as per Incident Reporting and Investigation procedure, section 5.5, all KU Employees are to be trained to recognize, observe and report near misses. The EHS Manager ensures that all employees receive this training through coordination with Departments. However, our review of 21 training modules for 2023 showed the absence of Incident/near miss reporting training module, which may result in employees not reporting the near misses that can turn into incidents. Father, there was an absence of Heat Injuries/stress and Illnesses Symptoms training in the module. Recommendation - Establish adequate and effective EHS training plan for KU employees, contractors, visitors, etc. - Conduct Incident and Near Miss reporting trainings to enhance Near Miss reporting culture. - Ensure coverage of Heat Injuries and Illnesses Symptoms training in the training modules. Management Action Plan Management Action Plan: Responsibility: Timelines: |  |
|  High | - EHS Site Visit |
| Risk Ref : KU-EHS-01 |  |
| Observation/Process Enhancement Based on our site visits in Main and SAN campuses conducted on 18th May 2023, we noted the following non-compliances: - Main Campus Findings - Electrical room in E building was open and not locked to prevent unauthorized access. - There was ongoing ‘working at height’ activity without a valid and approved PTW, and the employee was not wearing helmet which is a non-compliance to the Personal Protective Equipment procedure and Permit to Work procedure - In the firefighting system room, the firefighting diesel pump coolant level was found to be low as compared to the required level. The coolant level should be at “High” level in the coolant tank scale. Currently, the level is below “low” - Emergency contact numbers not updated at the temporary storage area next to the firefighting system room. Currently, the emergency contact numbers are for the old contractor which is a non-compliance to Emergency Management Contingency Plan - Some mechanical and electrical labs had exposed naked electrical wires. - In the industrial lab, the oil/lube bulk bottles were placed under the industrial compressed gas sources. - The Contractor team, Adeeb, were not wearing their PPEs (Gloves and helmets) while conducting HVAC PPM work as per permit requirements (PTW No. ADB/PTW/KUMC/032-23) and WO No. 100842 which is a non-compliance to the Personal Protective Equipment procedure - KU Vivarium project- PPE (Gloves) were not available during hammering nails activity and drilling activity which is a non-compliance to the Personal Protective Equipment procedure - KU Vivarium project- contractor employee was working at height without wearing required PPE (Gloves, Helmet, safety belt, etc.). Also, there was no PTW issued for this working at height. Currently, the EHS team does not have a working at height procedure that defines the work at height processes and precautions. - SAN Campus Findings - Firefighting system diesel pump coolant level was low. The coolant level should be at “High” level in the coolant tank scale. Currently, the level is below “low” - In the campus clinic, Medicine "Diclogesic" was found expired in April 2023. - Building 3 - Ruwais, had expired sanitizer in the first aid box - Petroleum refinery lab (3013 A) had expired medicine "response beta" in the first aid box - The First Aider displayed in the chemical lab, was on leave and there is no alternate first aider number displayed which is a non-compliance to Emergency Management Contingency Plan - Chemical Lab (3021) had expired medicine (Broad Spectrum Biocide) in the first aid box - Unlabeled chemical containers are in the Chemical lab (3021) - Arzanah building, the electrical room was open and not locked for unauthorized personnel. Recommendation - Ensure adequate and effective compliance to the procedures and work controls and ensure safe working conditions at site including fire pump rooms, clinics, buildings under construction, electrical rooms, and laboratories. Management Action Plan Management Action Plan: Responsibility: Timelines: |  |
|  Medium | - Audit & Inspection |
| Risk Ref : KU-EHS-14 |  |
| Observation/Process Enhancement - As per OSHAD, Audit and Inspection, Section 6, the entity non-conformance, and corrective actions shall address the following, at a minimum: - Identifying and correcting non-conformity(s) and taking actions(s) to mitigate their OSH consequences. - Means to report potential non-conformances at appropriate levels throughout the organization. - Means to record, monitor and manage all reported non-conformances appropriate to the OSHMS. - Investigating non-conformity(s), determining their root cause(s) and taking actions to avoid their reoccurrence. - Evaluating the need for action(s) to prevent non-conformity(s) and implementing appropriate actions designed to avoid their occurrence. - Recording and communicating the results of corrective action(s) and preventative action(s) taken; and - Reviewing the effectiveness of corrective action(s) and preventative action(s) taken as part of the close-out procedure. Our review of the EHS inspection records showed inadequate follow up mechanism (post inspection) to track the open/closed corrective actions covering all the inspection reports which may lead to repetitive incidents in future. Further, the inspection records are not signed and the section "followed by" (person who will conduct follow-up of corrective actions) was also not filled. In addition, our review of an EHS Internal Audit report "FDEHS/REP09-21/OCT/2022", 64 Minor Non-Conformance Report (NCR) and 29 Areas for Improvement (AFI) were identified. However, there were no action plans, target dates and status have been created in the Internal Audit tracker resulting in potential inadequate closure and implementation of identified corrective actions. Refer to Appendix 5 for further details. - Our review of 10 samples of inspection records showed in 3 out of 10, inspections were not conducted as per the inspection plan. Further, on detailed review of 6 inspection reports, delays were noted in sharing the inspection report with stakeholders resulting in the target dates and correction actions are not being tracked and monitored for implementation. Refer to Appendix 6 for further details. Recommendation - Establish inspection follow-up mechanism to track the open/closed corrective actions of all inspection reports. - Ensure the inspection reports are signed by the inspector and the concern stakeholders. - Ensure that the EHS Internal Audit tracker captures all internal audit findings related to EHS function and explore the possibility of automating the tracker to send notifications and highlight pending findings for resolution. - Ensure conducting of EHS inspections as per the inspection plan and implementation of effective follow ups of corrective action plans. Management Action Plan Management Action Plan: Responsibility: Timelines: |  |
|  Medium | - Permit to Work (PTW) |
| Risk Ref : KU-EHS-16 |  |
| Observation/Process Enhancement Permit to Work (PTW) is a process designed to identify, communicate, mitigate, and control risk in hazardous areas, nonstandard situations, and potentially hazardous conditions, such as shutdowns, to prevent accidents. Permit to Work systems are essential to frontline worker safety. As per the Permit to Work Procedure, KU–FD–EHS–MPM–07, the scope of PTW covers the following: - The period for completion of the work is not exceeding the maximum duration of the Permit to Work as defined by the start and end time. - For the work to extend beyond the stated finish time, the Permit to Work will be re-validated (including re-approval by the person issuing the Permit to Work) or a new Permit to Work issued. - The Permit to Work system only allow for limited extensions or revalidations rather than continuously extending previous Permit to Work. During our review of the PTW register, it was noted that 6 out of 70 PTWs in SAN are still "Open" since 2022 without re-evaluating the hazards arising due to changes in the work set-up. Refer to Appendix 7 for further details. Recommendation Ensure effective monitoring of permits to work and closure of permits without delays. Ensure permits extension is recorded in the permit to work form and ensure activity descriptions are recorded in the permit to work register. Management Action Plan Management Action Plan: Responsibility: Timelines: |  |
|  Low | - Legal Compliance |
| Risk Ref : KU-EHS-06 |  |
| Observation/Process Enhancement As per the Identification and Access to Legal and Other Requirements Procedure " KU–FD–EHS–MSM–02", Section 5.1, Legal and other requirements as applicable to KU operations, regarding the requirements of the EHS Management System, Environmental aspects and Occupational Health and Safety requirements are identified by EHS Department. EHS Function identifies, tracks, and maintains a list of all applicable legal and other requirements as applicable to KU operations. Our review of the EHS Legal and Other Requirements Register (KU-DF-EHS-REG-02) Rev. 04, Dated 18 Oct 2022, it was noted that below requirements applicable to KU’s operations were not identified: - Federal Law No. 33 of 2021 on Employment Relationship. - UAE Ministerial Resolution No. (505) of 2012 on Issuing the Regulation of the Cabinet Resolution No. (24) of 2012 concerning Regulating Civil Defense Services in the State. - Federal Law No. 12 of 2018 on the Integrated Waste Management. - Federal Law No. 12 of 2006 - Article 2, regarding the emission or the leakage of the Gaseous and Solid Pollutants and vapors to the ambient air was not identified in the EHS Legal and other requirements Register. This may result in inability to maintain the compliance with applicable EHS legal requirements leading to reputational loss / financial penalties and legal proceedings. Note: Above legal requirements were added to the legal register post audit report issuance. Recommendation Review and Update the Legal register identifying all the EHS applicable legal and other requirements. Further, ensure adequate reporting over compliance with such laws to Compliance / Legal Function. Management Action Plan Management Action Plan: Responsibility: Timelines: |  |

Appendix

Appendix 1

Findings Rating

The audit findings have been grouped together in a logical manner to appropriately convey the risk and impact. The audit findings have been categorized based on their criticality rating as High, Medium and Low. The definitions of the findings criticality / distribution are provided in the table below

|  | Finding Rating | Definition | Number of Findings | Total |
| --- | --- | --- | --- | --- |
|  | High | Finding is serious and deserves immediate attention by the Process Manager. The finding is reported to the Audit Committee quarterly. | 2 | 9 |
|  | Medium | Finding impacts the accomplishment of the Process objectives. Corrective action is required by management. If not resolved, the finding could result in inefficient use of entity resources and or potentially disrupt business processes. | 6 |  |
|  | Low | Finding to be reported to Management but is of a minor risk to the entity. Findings will not be reported to the Audit Committee unless the finding remains open after the follow up audit. | 1 |  |

Appendix 2 – List of outdated EHS Policies and Procedures

These policies and procedures relate to occupational health, well-being, emergency management, hazardous material management, first-aid, EHS risk assessment, PPEs to be used, etc. Procedures such as Electrical Safety Procedure, and First Aid Procedure needs to be updated. Also, Work at Height Procedure needs to be developed and established. Outdated policies and procedures may result in inconsistent EHS practices being followed by staff & contractors, thereby increasing the risk of EHS incidents.

| Sr No | Policy Name | Policy Description | Approval Date |
| --- | --- | --- | --- |
| 1 | EHS-7400 Environment, Heath Safety | Improving the environmental, health and safety performance of its activities. | 1-Jan-18 |
| 2 | EHS 7450 Occupational Health and Safety | Occupational health, safety, and welfare of all of its staff members and those affected by its activities including students, visitors, contractors, and members of the public. | 1-Jan-18 |
| 3 | EHS 7500 Health and Well-Being | Health and wellbeing of Faculty, staff, volunteers, and campus contractors across all KU campuses. | 1-Jan-18 |
| 4 | EHS 7510 Smoke Free Environment | Smoke free environment | 1-Jan-18 |

| Sr No | Procedure Name | Last Review Date |
| --- | --- | --- |
| 1 | Communication Participation and Consultation | 2018 |
| 3 | Control of Records | 2018 |
| 4 | Document Control Procedure | 2018 |
| 5 | EHS Audit Internal & External | 2018 |
| 6 | EHS Design and Modification | 2018 |
| 7 | EHS Implementation Plan | 2018 |
| 8 | EHS Objectives and KPI's | 2018 |
| 9 | EHS Operational Control Procedure | 2018 |
| 10 | Emergency Evacuation Plan | 2018 |
| 11 | Emergency Management-Contingency Plan | 2018 |
| 12 | Emergency Preparedness Procedure | 2018 |
| 13 | Environmental MS Interested Parties | 2018 |
| 14 | Evaluation of Compliance | 2018 |
| 15 | First Aid | 2018 |
| 16 | Hazardous Material Management | 2018 |
| 17 | Identification of Legal and Other Requirements | 2018 |
| 18 | Incident Reporting and Investigation | 2018 |
| 19 | Management of Change | 2018 |
| 20 | Management Review | 2018 |
| 21 | Managing the Risk of Plant | 2018 |
| 22 | Manual Handling | 2018 |
| 23 | Non-Conformities Corrective Preventive & Improvement Action | 2018 |
| 24 | Occupational Health & Safety | 2018 |
| 25 | Performance Monitoring, Measurement and Reporting | 2018 |
| 26 | Permit to Work | 2018 |
| 27 | Personal Protective Equipment | 2018 |
| 28 | Risk Assessment Procedure | 2018 |
| 29 | Roles and Responsibilities Procedure | 2018 |
| 30 | Training Competence and Awareness | 2018 |
| 31 | Waste Management | 2018 |
| 32 | Working Alone and After-Hours work in Laboratories | 2018 |
| 33 | Workplace Inspection Procedure | 2018 |
| 34 | EHS Electrical Safety Management Procedure | 2018 |

Appendix 3 – EHS Management Review Agenda 2022

| Department Name | S/N | Objectives Details | Measuring Method | Target | Objective Evaluate |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Dec-22 |
| EHS | 1 | Attain one or more new national \ International award and or certification (different than ISO9001) | 1 Awards or Certificate | 22-Dec | 4 |
|  | 2 | 90% accomplishment EHS training of all KU community | 90% Completion | 22-Dec | 3 |
|  | 3 | Assure that 100% (minimum completion of 80% on monthly plan) of all KU Assets, Equipment & Instrumentations are calibrated, or PAT testing conducted in line with EHS compliances | 100% Completion | 22-Dec | 3 |
|  | 4 | Achieve 100% compatibility with national standards | 100% Compatibility | Dec 2022 | 3 |
|  | 5 | Increase the recycle of general waste to 30% | Recycle 30% | 22-Dec | 3 |
|  | 6 | Establish Energy Management Plan & Sustainable Practices for every facility in KU | 100% Completion | 22-May | 3 |
|  | 7 | Target 3% reduction of Energy consumption from the previous year | 5% Energy Saving | 22-Dec | 3 |
|  | 8 | Develop on-job training plan targeting 30% of the department job responsibilities/resources by Feb 2022. Establish implementation to achieve 90% of the set plan | 90% as per Set Plan | 22-Dec | 3 |
|  | 9 | Complete full Integrated of Facilities Management CAFM Solution | 100% Completion | 22-Jul | - |
|  | 10 | Develop Integrated Quality Management System and achieve ISO 9001 or more (ISO standard , APPA and RICS) | 100% Completion | 22-Dec | 3 |
|  | 11 | Propose 3-5 enhanced in department policy, process & procedures to achieve time reduction, cost saving, customer satisfaction, service quality improvement. | 3-5 proposals | 22-Dec | 3 |
|  | 12 | Develop enhanced functional unit level responsible matrix and apply departmental DoA | 100% Completion | 22-Sep | 3 |
|  | 13 | Implement periodical One-to-One staff meeting with the line manager and submit the improvement action plan | As per Yearly Plan | Monthly | 3 |
|  |  |  |  |  | 62% |

Appendix 4 – Inconsistencies in the Incidents and Near Misses Reported in 2022

| Reporting Parties | Number of Reports | Number of Property Damage | Number of Near Misses |
| --- | --- | --- | --- |
| OSHAD Reports | (Q1+Q2+Q3+Q4) | 1 | 7 |
| Sample Contractor EHS Statistics Performance Report | (4 report samples in Oct and Dec 2022) | 6 | 38 |
| EHS List of Incidents 2022 |  | 1 | 4 |

Appendix 5 – Number of Findings in the Internal Audit Report in 2022

| Findings | Number |
| --- | --- |
| Positive Points | 30 |
| Major Non-conformity | 0 |
| Minor Non-conformity | 64 |
| Area for Improvement | 29 |

Appendix 6 – Field Visit Findings of the Sample Inspection Records

| Sr. No | Timeline (2023) | Inspection | Main /SAN | Lab /Building | Field Visit Findings as on 13 June 2023 |
| --- | --- | --- | --- | --- | --- |
| 1 | Q1 | Chemistry (1) | Main | Lab | Inspection not conducted |
| 2 | Q1 | Chemical Engineering (1) | Main | Lab | Inspection not conducted |
| 3 | Q1 | Electrical Engineering & Computer Science (17) | Main | Lab | Conducted on 14th March and action target date is 20th April. However, Email with the Inspection report was sent to stakeholder on 12th May (delay of 2 months after inspection date and 23 days after expected completion date of action plan) |
| 4 | Q2 | Medical Simulation (30) | Main | Lab | Absence of target date for 10 corrective actions |
| 5 | Q2 | Building K | Main | Building | Helpdesk status shows status of corrective actions is in progress. The target date for closing of corrective action was 11th April, however, actions were not closed as of 13th June (delay of 63 days) |
| 6 | Q2 | Electrical Engineering & Computer Science Labs (7) | SAN | Labs | Inspection not conducted |

Appendix 7 – Permit to Work Findings of 2022 PTW Tracker

| Sr. No | PTW No. | PTW Date | Activity | Findings |
| --- | --- | --- | --- | --- |
| 1 | 042/ 2022 SAN | Jul. 22, 22 | Waterproofing at Roof | Status is "Open" since 22 July 2022. Also, the PTW extension was till March 31 2023. However, the extension was not mentioned in the PTW form, and the permit is still open |
| 2 | 051/ 2022 SAN | Sep. 10, 22 | Supply and Installation of the Power Supply for Office Relocation & Electrical work | Status is "Open" since 10 Sep. 2022. PTW extension was till April 30 2023. However, the extension was not mentioned in the PTW form, and the permit is still open |
| 3 | 064/ 2022 SAN | Nov. 14, 22 | Installation of gasifier pilot plant. | Status is "Open" since 14 Nov. 2022. |
| 4 | 067/2022 SAN | Dec. 07, 22 | Civil foundation for Pump and watering | Status is "Open" since 7 Dec. 2022. |
| 5 | 069/2022 SAN | Dec. 14, 22 | Removing scrap | Status is "Open" since 14 Dec. 2022. |
| 6 | 068/2022 SAN | Dec. 08, 22 | - | Status is "Open" since 8 Dec. 2022. Also, there was no Permit, and activity description was not mentioned |